# Environmental Risk Assessment

This assessment covers the proposed non-hazardous waste plastic reception, storage and treatment activities at Chequerbent Works. The supplied EMS identifies manual and mechanical sorting/separation, shredding, heated granulation, bagging, wrapping and loading/unloading. Waste types are HDPE, LDPE film, PE scrap, baled film, bagging waste, trims/offcuts and purge/regrind under codes 15 01 02, 20 01 39, 19 12 04 and 07 02 13. No hazardous, clinical or liquid wastes are accepted. The EMS states a maximum storage capacity of 275 tonnes and an annual manufactured output of approximately 18,032 tonnes.

The site is an established industrial premises. The EMS describes commercial/industrial land uses on three sides and residential properties on one side. The FPP additionally identifies surrounding industrial/commercial premises, residential dwellings, the A58/A6/M61 road network, the East Lancashire railway line, nearby leisure/retail uses and surface waters as receptors.

## Risk assessment methodology

Each risk is considered using the source-pathway-receptor approach. Existing controls in the EMS/FPP are treated as the primary mitigation. Residual risk is expressed qualitatively as Low, Medium or High after controls.

| Hazard/source | Potential event | Pathway | Receptor | Residual risk | Controls |
| --- | --- | --- | --- | --- | --- |
| Surface water pollution | Spills, contaminated runoff, firewater | Yard/drainage network and overland runoff | Surface waters; drainage system | Low | Waste capable of polluting runoff stored on concrete operational area; bunded fuel; spill kits; daily surface inspections; firewater containment procedures; CCTV drain survey and drainage plan. Firewater to be contained and removed by tanker following an incident. |
| Groundwater / land contamination | Fuel/oil leaks, spills, waste handling | Defective surface or drainage, infiltration to ground | Soil and groundwater beneath site | Low | Established industrial site; concrete operational surfaces; bunded fuel storage (110% capacity); pipework within bund; spill kits; daily inspections; no hazardous or liquid waste accepted. Any spill is contained, cleaned and contaminated absorbent removed to an authorised facility. |
| Fire and smoke | Combustible plastic waste, plant/equipment, ignition | Airborne smoke/particulate; runoff of firefighting water | Residents, workers, businesses, roads, railway, surface waters | Low-Medium | Dedicated FPP; storage bays/fire separation; 24/7 monitoring/CCTV; sprinkler system; extinguishers, hoses and hydrant provision; quarantine area; firewater containment. FPP calculates 73 m3 containment requirement for the largest pile. |
| Dust / particulate | Vehicle movements, unloading, processing, shredding, granulation | Air | Nearby businesses, residents, site users | Low | Sheeting where necessary; wet cleaning; minimise stockpiles and drop heights; water supply for suppression; continuous operative observation and formal visual inspections at least three times per day; immediate cleaning of deposits. |
| Litter | Light plastic film and packaging waste | Wind | Neighbouring land, highway, residents/businesses | Low | Daily litter inspections; light waste placed in skips; checks beyond boundary; sealed skip used in high winds; prompt collection of windblown material. |
| Odour | Unexpected malodorous/non-conforming load | Air | Residents and nearby businesses | Low | Plastic waste stream has low inherent odour potential; strict turnaround; malodorous material rejected/quarantined or removed immediately; complaints procedure. |
| Noise and vibration | HGVs, loading/unloading, mobile plant and processing equipment | Air/ground | Residential and commercial receptors | Low | HGV movements spread through day; 5 mph site limit; engines off when not required; plant/vehicles maintained and silenced; white-noise reversing alarms preferred; no body shaking; drop heights minimised. EA has advised that a separate Noise Impact Assessment is not required. |
| Mud/debris on highway | Vehicle movements and material handling | Vehicle tracking / wind | Public highway and drainage | Low | Daily inspection of vehicle running surfaces; deposits treated as an emergency and cleaned promptly; silt not washed into roadside drains/gullies. |
| Fuel/oil storage | Diesel/fuels and vehicle maintenance materials | Leak/spill to surface/drain/ground | Land, groundwater and surface water | Low | Bunded tank with minimum 110% capacity; pipework within bund; locked valve; tank separated from waste processing; secure storage of oils/chemicals; spill response equipment. |
| Unauthorised/non-conforming waste | Concealed drums, hazardous/liquid or reactive waste | Spill, reaction, emissions | People, land, water, air | Low | No hazardous, clinical or liquid wastes accepted; waste acceptance procedures; quarantine/rejection; stop further deposits; identify producer and contact EA where necessary; spill containment; emergency/specialist assistance where required. |
| Pests/scavengers | Stored waste | Direct access | Neighbouring premises/amenity | Low | Daily inspections; pest controller engaged if evidence is found. Plastic-only waste presents limited attraction. |
| Flood/firewater escape | Firefighting water | Yard and drainage | Surface water, land, neighbouring property | Low | FPP provides containment calculation and procedure. Firewater pools/ponds in yard/building; temporary drainage protection deployed; standing water removed by vacuum tanker to suitably permitted treatment facility. |

## Drainage condition qualification

The April 2026 CCTV drainage survey identifies surface-water and combined drainage sections and records defects in parts of the existing underground network, including fractures, displaced joints, broken/collapsed sections and abandoned survey runs. For that reason this assessment does not rely on a blanket assertion that every underground pipe is impermeable. Pollution prevention is based on the controlled concrete operational area, spill prevention/response, bunding, firewater containment, drainage management and inspection/maintenance of the drainage network.

## Conclusion

With the controls described in the EMS, FPP and this assessment implemented and maintained, the identified environmental risks are considered capable of being controlled to a low or low-medium residual level. The assessment must be reviewed following a significant incident, material change to waste types/quantities, site infrastructure, drainage or treatment activities, or where monitoring/complaints indicate that existing controls are not effective.