FIRE PREVENTION PLAN 2026

FIRE PREVENTION PLAN (FPP): CORE FUSION LIMITED

Location: Haven Road, CO2 8HT

Edition: 5th Edition (October 2026)

Author: Leila Music-Dicker

### 1. Activities

- Waste Acceptance

- Disposal of Non-Hazardous Waste

- Sorting and Segregating Waste

- Waste Processing

- Waste Removal from Site

- Waste Processing (Bailing)

### 2. Managing Common Causes of Fire

- Arson

- Plant and Equipment

- Electrical Sparks

- Smoking

- Hot Works

### 3. Preventing Self-Combustion

- Separation

- Stock Rotation

- Storage Limit

- Temperature & Moisture Monitoring

- Quarantine

- Response

- Routine Activities (Daily, Weekly, Monthly)

- Site Policies

- Plant and Vehicle Maintenance

- Roles and Responsibilities

- Emergency Quick-Reference Table

- Recognising Combustible Waste (EWC Codes)

### 4. Managing Waste Piles

- RORO Dimensions

- Total Site Capacity

- Quarantine Areas

### 5. Waste Monitoring and Storage Limits

- 5.1 Storage Durations and Temperature Limits

- 5.2 Handling of Overheating Waste

- 5.3 Storage Specifications

- 5.3.1–5.3.4 Container and Concrete Bay Specifications

- 5.4 Fire-Specific Design Features

- 5.5–5.6 Fire Safety Justification and Firewater Containment

### 6. Fire Detection and Suppression

- Active Monitoring

- Out-of-Hours Security

### 7. Water Supplies

- 7.1 Water Supply & Fire Suppression Strategy

- 7.2 Site Layout & Accessibility

- 7.3 Onsite Suppression Equipment

- 7.4 Water Supply Requirements

### 8. Managing Fire Water Run-off

- 8.1 Firewater Containment & Environmental Protection

- 8.1.1 Primary Containment: Front Entrance (Aqua Dam)

- 8.1.2 Secondary Containment: Rear & External Areas

- 8.1.2 Drainage Protection

- 8.2–8.3 Containment Capacity Calculations

- 8.4 Post-Incident Procedures & Disposal

### 9. Contingency and Recovery

- During a Fire

- After a Fire

### 10. Staff Training

- Induction & Toolbox Talks

- Fire Drills

- Shadowing

- Supervision

1. ACTIVITIES

1.1 Waste Acceptance

- Source: Waste is delivered from residential and commercial sites in skips.

- Categorization: EWC codes are applied at collection and confirmed upon arrival.

- Storage: The facility is used for processing and segregation before it is moved on to Recycling/ Recovery/ Disposal sites. Minimal bailing of cardboard only

- Record Keeping: Waste is checked and recorded by skip volume before being unloaded onto the concrete tipping floor within the building.

1.2 Disposal of Non-Hazardous Waste

- Screening: Waste is screened for non-conforming items. These are immediately removed, labelled with the address of origin, and returned within 5 working days.

- Disposal Partners:

  - CSH Environmental: Plastic

  - Birch Airfield Composting: Green waste (weighed on arrival).

  - Silverton: Hardcore and soil (stored in 20-yard RORO and disposed of when full).

  - Autobreak: Metal and electrical cable (weighed on arrival).

  - Indaver: small municipal waste, sent for incineration

  - Enovert: Large municipal waste, deposited to land (5%)

  - FCC: wood recycling

  - Bolton Brothers:  Cardboard

1.3 Sorting and Segregating Waste

- Process: Waste is segregated into small piles on the internal hard-standing floor and moved into designated RORO using 360, grab and loading shovel.

- Monitoring: Volumes are monitored in m³. Removal is scheduled once a RORO is 75% full (excluding freeboard space).

- Safety Features: * RORO BINS are separated by alternating combustible and non-combustible waste with a 1m freeboard space above the waste.

  - Capacity: Each RORO allows a maximum storage of 30.58m³.

  - Roro Positioning: Disposal RORO’s alternate between combustible and non-combustible materials to increase safety. RORO’s are positioned near water hoses and fire extinguishers, based on type of waste stored.

1.4 Waste Processing

- Daily Tasks: Processed waste is moved from the tipping area to designated RORO’S as soon as it is sorted.

- Recovery: Recovered materials (copper, aluminium,) are stored in skips or tonne bags for recycling.

- Safety: Personal Protective Equipment (PPE) must be always worn.

1.5 Waste Removal from Site

- Frequency: Removal is scheduled weekly or when RORO’s reach 75% capacity to ensure safety and good timekeeping.

- Method: A "First In, First Out" (FIFO) basis is used for all waste.

- Documentation: Transfer notes are created for every movement, stapled for records, and uploaded for EA (Environment Agency) returns quarterly.

1.6 Waste Processing (Bailing)

- Frequency: Weekly when the RoRo is half full

- Method: The bales of cardboard will be made with a small industrial mill size baler. The baler operator will receive full training in creating bales safely. When baler is not in use it will be moved into the back yard and disconnected from power supply.

- Documentation: Bales are recorded to ensure they are not stored on site for longer than 60 days. They will then be transported to Bolton Brothers, Ipswich, for recycling.

2. MANAGING COMMON CAUSES OF FIRE

2.1 Arson

The Core Fusion facility is situated within an industrial zone, bordered by aggregate processing centres and a wastewater treatment plant. Access is strictly controlled via a primary lockable gate on Haven Road and a secondary security fence with a gated entrance on the private access road.

Site security is managed through a multi-layered approach:

- 24/7 Surveillance: High-definition CCTV covers the entire perimeter and all entry points. This system is remotely monitored by a third-party security firm.

- Physical Patrols: A security contractor conducts two physical site inspections every night.

- Internal Monitoring: The building interior—including waste storage areas, offices, and the kitchenette—is equipped with motion-detecting cameras.

- Fail-Safe Protocols: The internal Wi-Fi-connected system features automated alerts. If a system failure occurs, the company directors are notified immediately via mobile. Given their 15-minute proximity to the site, they are available to perform manual inspections and system resets at any hour.

2.2 Plant and Equipment

All plant and equipment is fitted with or in proximity of fire extinguishers which are checked and serviced yearly. All equipment and plant are checked daily for any leaks and cleaned out twice a day to remove dust that may gather due to the nature of work.

2.3 Electrical Sparks

All electrical equipment is tested yearly (PAT test) as well as electrical wiring and plugs. All other ignition sources are kept a safe 6m distance from waste, unless actively working on it ( 360 with grab and shovel loader). When not in use plant is parked, ignition turned off and safe 6m distance observed.

2.4 Smoking

Core Fusion Limited has a strict No Smoking Policy for entire site.

2.5 Hot Works:

Any Welding of skips is carried out in the back yard, which is away from all the waste. The work is only carried out by a competent welder with up to date certification and permit to work. We observe a strict 1-hour fire watch post work. Welding area has 3 fire extinguishers to ensure any fire that may be caused by hot rock or otherwise is put out immediately.

3 PREVENTING SELF-COMBUSTION

- Separation: A 6m safe distance must be maintained between combustible waste and ignition sources.

- Stock Rotation We operate a "first-in, first-out" policy.

- Storage Limit: Waste must not be stored for longer than 90 days.

- Temperature Monitoring: Mid-section and outer temperatures must be checked daily and recorded on monthly sheets.

- Moisture Monitoring: waste is routinely rotated to ensure drying out. Due to low storage ability, 90% of waste is disposed of a minimum of once a week.

- Quarantine: Loose waste on the floor must be pushed into the quarantine area if a fire occurs to prevent spreading.

- Separation in case of fire: As all waste is contained in RORO’s the burning bin can be quickly and safely isolated from any other waste, increasing the chance of extinguishing the fire and reducing the risk of fire spreading and further risk of environmental damages.

- Response: The Fire and Rescue Service must be contacted immediately whenever a fire is detected. Only competent staff may tackle a small fire, and only where it is safe to do so without delaying the alarm, evacuation or emergency call.

3.1 Routine Activities (Daily, Weekly, Monthly)

- Fire Drills: Held on the first Monday of every month.

- Shutdown Procedure: All plant must be switched off 30 minutes before closing to allow for a monitored cooling period.

- After-Hours Deliveries: Full skips delivered after 4:00 PM must stay in the skip inside the building, be uncovered, and have their temperature checked.

3.2 Site Policies

- Smoking: A strict "No Smoking" policy is in effect on-site and within 10 meters of the perimeter.

- Flammable Materials: Gas cylinders and chemicals must be stored in caged, bunded areas at least 6m from combustible waste. Any cylinders found in skips must be moved to quarantine and removed within 24 hours.

- Visitors: All visitors must report to the reception and follow the site plan for disposal of waste.

3.3 Plant and Vehicle Maintenance

- Daily Checks: Visual inspections for leaks (oil/hydraulic), lifting gear functionality, and warning lights are mandatory before and after shifts.

- Parking: All vehicles and plant must be parked at least 6m away from combustible waste overnight.

- Weekly Maintenance: Plant must be greased weekly and hydraulics repaired immediately if damaged.

- Maintenance service: to be carried out by competent service personnel only, as per manufacturer’s advice

- Safe Shutdown: Keys must be removed from ignitions, lights switched off, and buckets/arms lowered to the ground when not in use.

3.4 Roles and Responsibilities

To ensure the effectiveness of the Fire Prevention Plan and compliance with safety standards, the following roles and responsibilities are assigned:

3.4.1. Site Manager

- Oversees implementation of the Fire Prevention Plan.

- Ensures all staff receive induction training and regular toolbox talks.

- Maintains up-to-date records of fire drills, maintenance checks, and temperature logs.

- Acts as primary contact for emergency services and regulatory authorities.

- Reviews and updates the Fire Prevention Plan annually or after any incident.

3.4.2. Waste Acceptance Officer

- Verifies EWC codes and checks waste upon arrival.

- Logs skip volumes and ensure proper unloading procedures.

- Identifies and isolates non-conforming waste for quarantine and removal.

3.4.3. Sorting and Processing Team

- Segregates waste into designated RORO bins, maintaining safe distances and freeboard space.

- Monitors waste volumes and schedules removal when bins reach 75% capacity.

- Ensures PPE is always worn during waste handling.

3.4.4. Plant and Equipment Operator

- Conducts daily visual inspections for leaks, warning lights, and lifting gear functionality.

- Parks vehicles and plant at least 6m from combustible waste overnight.

- Performs weekly maintenance and immediate repairs as needed.

- Ensures safe shutdown procedures are followed.

3.4.5. Fire Safety Officer

- Conducts daily and seasonal fire risk checks, including temperature and moisture monitoring.

- Maintains and tests fire detection and suppression equipment (extinguishers, alarms, hose reels).

- Coordinates monthly fire drills and documents outcomes.

- Oversees quarantine procedures during fire incidents.

3.4.6. Security Personnel

- Performs nightly site patrols and monitors CCTV systems.

- Responds to system alerts and coordinates with site managers for manual inspections.

3.4.7. All Staff

- Adheres to site policies, including no smoking and safe handling of flammable materials.

- Reports hazards, near misses, or incidents immediately to the Site Manager or Fire Safety Officer.

- Participates in training, drills, and shadowing as required.

## Emergency Quick-Reference Table

| Emergency Situation | Immediate Actions | Responsible Role | Key Contacts | Essential Equipment |
| --- | --- | --- | --- | --- |
| Fire Detected | - Raise alarm - Evacuate staff - Contact Fire & Rescue - Isolate burning waste (if safe) - Deploy fire suppression | Fire Safety Officer All Staff | Fire & Rescue Services Site Manager | Fire extinguishers Hose reels Thermal probe |
| Waste Overheating | - Rotate/turn waste - Water down (last resort) - Place Hydro Snake bags - Record incident | Sorting Team Fire Safety Officer | Site Manager | Thermal probe Hydro Snake bags Absorption pads |
| Arson/Security Breach | - Secure site - Contact security - Notify Site Manager - Review CCTV footage | Security Personnel | Security Contractor Site Manager | CCTV system Lockable gates |
| Hazardous Waste Found | - Move to quarantine - Label and isolate - Arrange removal within 24 hours | Waste Acceptance Officer | Site Manager | Quarantine area Labels |
| Fire Water Run-off | - Deploy Aqua Dam - Seal drains - Contact Bio Marsh for removal | Fire Safety Officer | Bio Marsh Contractor Site Manager | Aqua Dam Neoprene drain covers |
| Evacuation | - Lead staff to assembly point - Account for all personnel - Await all-clear | Site Manager All Staff | Fire & Rescue Services | Site map Assembly point sign |
| Post-Incident Recovery | - Stop waste acceptance - Dispose of fire-damaged waste - Review plan and update | Site Manager | Environment Agency Site Manager | Incident log Updated FPP |

3.5 Recognising Combustible Waste (EWC Codes)

| Waste Type | EWC CODE | AUTO IGNITION TEMPERATURE |
| --- | --- | --- |
| CARDBOARD & PAPER | 20 01 01 | 218°C – 246°C |
| PLASTIC | 20 01 39 | 350°C – 500°C |
| WOOD | 20 01 38 | 200°C – 300°C |
| TEXTILES (RUGS/CARPETS) | 20 01 11 | 250°C – 450°C |
| TEXTILES (CLOTHES) | 20 01 10 | 250°C – 400°C |
| MUNICIPAL WASTE | 20 03 01 | 200°C – 300°C |
| TYRES | 16 01 03 | 400°C – 480°C |
| ELECTRICAL WASTE | 20 01 36 | 300°C – 500°C |
| GREEN WASTE | 20 01 02 | 150°C – 250°C |

4. MANAGING WASTE PILES

4.1 RORO Dimensions

The site utilizes a maximum of 10 storage RORO’S. All RORO’S include a 1m freeboard for safety.

| Containment Type | Waste Type | Width (mm) | Depth (mm) | Max Height (mm) | Volume (m³) |
| --- | --- | --- | --- | --- | --- |
| LOOSE (bay) | C-Grade Wood | 7000 | 7000 | 4000 | 196 |
| RORO | Plasterboard | 2400 | 6200 | 2700 | 30.6 |
| RORO | MUNICIPAL WASTE (INCINERATOR) | 2400 | 6200 | 2700 | 30.6 |
| RORO | MUNICIPAL WASTE (LANDFIL) | 2400 | 6200 | 2700 | 30.6 |
| RORO | Cardboard | 2400 | 6200 | 2700 | 30.6 |
| RORO | Green Waste | 2400 | 6100 | 2700 | 30.6 |
| RORO | Soil | 2400 | 2200 | 1800 | 15.29 |
| RORO | Hardcore | 2400 | 2200 | 1800 | 15.29 |
| RORO | Metal | 2400 | 2200 | 1800 | 15.29 |
| SKIP | Aluminium/Copper | 1750 | 3700 | 1700 | 9.17 |

Total Site Capacity: 404.04m³.

4.2 Quarantine Areas

- Internal Quarantine (6m²): Used for non-conforming waste, isolating fire risk, or daytime plant parking. It can hold one 40-yard roro.

- External Quarantine (42m²): Located in the secure front yard. It can hold up to 36m³ of waste (equivalent to 120% of the largest pile on site).

5. WASTE MONITORING AND STORAGE LIMITS

5.1 Storage Durations and Temperature Limits

| Waste Type | Max Storage | Max Temp (°C) |
| --- | --- | --- |
| General Waste | 7 Days | 50° |
| C-Grade Wood | 21 Days | 50° |
| Ferrous Metals | 30 Days | 50° |
| Plastics | 30 Days | 50° |
| Metals/Cables (Tonne Bags) | 60 Days | N/A |
| Cardboard | 60 Days | 50° |
| Green Waste | 30 Days | 50° |
| Soil / Hardcore | 1-2 Days | N/A |
| Plasterboard | 60 Days | N/A |

5.2 Handling of Overheating Waste

If temperatures exceed limits:

- Rotation: Waste must be rotated or turned over with a plant to lower the temperature.

- Watering: As a last resort, waste can be watered down.

- Containment: Hydro Snake bags must be placed at exits to prevent runoff from escaping the building overnight. Any wastewater must be collected with absorption pads which can be discarded in general waste for incineration

5.3 Storage of Waste Specifications of RORO

Technical Specification: 40-Yard RoRo Waste Container

5.3.1. Material Properties (Mild Steel)

- Primary Material: S235 or S275 Grade Mild Steel (standard structural grade).

- Melting Point: 1,425°C – 1,540°C.

- Thermal Softening Point: Approximately 550°C – 600°C (point at which the steel loses 50% of its structural yield strength).

- Surface Treatment: High-durability anti-corrosive primer and topcoat (typically 100-120 microns total) to prevent oxidation and thinning of the steel walls.

5.3.2. Physical Construction

- Floor Plate: 4mm or 5mm thick (heavier gauge used for floor to resist impact and "burn through" from hot loads).

- Side Walls: 4mm thick Mild Steel.

- Main Runners: 152mm x 76mm or 180mm x 75mm heavy-duty channel (Parallel Flange Channel).

- Vertical Ribs: Side uprights spaced every 600mm to 900mm to prevent "bulging" under the pressure of compacted waste.

- Welding: Continuous MIG welding on all structural seams to ensure the bin is liquid-retentive (essential for preventing contaminated fire-water runoff).

- Welded ladder to ensure waste temperature can be taken with a probe from above, ensuring correct measurements of the core of the pile.

- 5.3.3 Concrete Block Bay
Technical Specification: Concrete "Lego" Block Storage Bay 7m x 7m x 4m)

- Material Properties (Precast Concrete)

- Primary Material: C40/50 Grade Heavy-Duty Precast Concrete (in accordance with BS EN 206-1 and BS EN 13369).

- Compressive Strength: Minimum 50 N/mm² characteristic cube strength at 28 days.

- Fire Resistance: Class A1 Non-Combustible (BS EN 13501-1); minimum 120-minute fire barrier rating (REI 120) to satisfy Environment Agency Fire Prevention Plan requirements.

- Density: Nominal 2,400 kg/m³ dry density (high mass for gravity retention and impact resistance).

- Exposure Class: XC3/XC4 (Carbonation) and XF1/XF3 (Freeze-Thaw outdoor exposure to BS 8500-1).

- Interlocking Mechanism: Precision-moulded male studs on the top face and corresponding female recesses on the bottom face for shear key alignment and mortarless placement.

- 5.3.4. Physical Construction

- Bay Dimensions: 7.0m (Internal Clear Width) x 7.0m (Internal Clear Depth) x 4.0m (Overall Wall Height). 3-sided "U-Shaped" freestanding configuration, with 1m of freeboard as fire break

- Block System: 1,600mm (Length) x 800mm (Width) x 800mm (Height) standard block system (1.024 m³ volume per standard block).

- Wall Thickness: 800mm single-skin dry-laid construction.

- 5.4 Fire-Specific Design Features

5.4.1 RORO

- Door Seals: Heavy-duty twin-door or top-hung tailgate with secondary locking pins to prevent door failure during a thermal event.

- Drainage Plugs: Often fitted with a 2-inch bung at the front or rear to allow for the controlled release of fire-water or to prevent the bin from becoming "over-weighted" during dousing.

- Standard Dimensions: Approx. 6.1m (Length) x 2.4m (Width) x 2.5m (Height).

- 1m freeboard to reduce the risk of fire spreading.

5.4.2 Lego Blocks

Fire Integrity & Rating:

Class A1 Non-Combustible construction (BS EN 13501-1). Achieves a minimum 120-minute fire resistance rating (REI 120) to satisfy Environment Agency (EA) Fire Prevention Plan (FPP) separation distance alternative guidance.

Thermal Mass & Containment:

High-density mass concrete (2,400 kg/m3) acts as a continuous thermal sink, absorbing radiant heat and preventing thermal transfer or auto-ignition of waste in adjacent containment bays.

Vertical Freeboard Margin:

Design incorporates a 1.0m minimum freeboard zone at the top of the 4.0m wall (maximum operational waste stack height limited to 3.0m). This prevents flame spillover, radiant heat ignition, or physical roll-over of burning material into adjacent bays.

Joint Sealing & Flame Penetration:

- Precision interlocking male/female nibs form a physical stepped joint, blocking direct line-of-sight flame paths and heat transfer between courses.

- Internal wall joints specified with fire-rated intumescent acrylic/silicone sealant or high-temperature ceramic fire-rope to prevent hot gas and ember migration through block seams.

Spall Resistance:

Designed with minimum 40mm concrete cover to internal reinforcement (if cast-in) or macro-synthetic fibre additives to reduce explosive spalling under prolonged high-temperature exposure during a 4-hour firefighting scenario.

Firewater Retention & Containment:

Direct dry-laid wall base forms a perimeter barrier to aid in containing contaminated firewater runoff when integrated with perimeter bunding, drain-mats, the bay will be equipped with a designated drains which will run into the sump of 5000L, which can be recirculated in case of a fire, and used for firefighting purpose only, the bay will be constructed with a gradient drop to further assist with water containment, a total of 6125L of water after the waste displacement is taken into the account

Post-Incident Structural Integrity:

Mass-gravity design maintains overall structural stability during severe thermal exposure and direct impact loads from Fire & Rescue Service (FRS) high-pressure hose jets or emergency loading shovel operations.

- 5.5 Fire Safety Justification

## 5.5.1 RORO

The storage containers used are 40-yard heavy-duty steel RoRo. Due to the high melting point of the S235/S275 mild steel (>1,400°C), the containers act as a fire-retardant skin. This helps contain 'deep-seated' fires within the waste mass. The 4mm wall thickness provides a thermal barrier that prevents immediate fire spread to adjacent bins, this will allow sufficient time to isolate the bin containing fire by moving it into the quarantine area and douse it with water. 

The fire water will be contained within the skip and can be disposed off safely without the risk of environmental contamination through run off.

5.5.2 Lego Block Bay

Waste wood will be stored unprocessed in the bay and removed once a week through a hauling company. Because wood will remain unprocessed (un-shredded), the risk of fire will remain low. It will also aid with the displacement of water within the bay as the gaps will be greater, thus reducing the risk of wastewater escaping into the environment. The bay will be slopped towards the end wall to create a lagoon type of storage, allowing to store approx.. 12,250 litres of water, furthermore, the drains will be installed outside of bay directly into 5,000l sump.

5.6 Containment of Firewater & Pollutants

5.6.1 Liquid-Retentive Container Design

- Sealed Construction: All 40-yard RoRo bins are specified with full continuous internal welds. This ensures that in the early stages of a fire, the bin acts as a "bund," holding any initial melted plastics or liquids.

- Integrity Checks: Monthly inspections are carried out to check for corrosion or holes in the 4mm floor plates that could compromise liquid containment.

5.6.2 Site Bunding and Drainage

- Impermeable Surface: All RoRo bins containing combustible waste are stored on Grade A reinforced concrete to prevent any seepage into the sub-soil and inside the building.

- Sealed Drainage System: During a fire event, the site drainage system will be closed using penstock valves or drain mats to prevent fire-water from entering the public sewer or local watercourses.

- Secondary Containment: Aqua Dam Measuring 10meters in length and 60cm in height, Aqua Dam will provide sufficient water containment in case of a fire breaking out. Aqua Dam can take a maximum of 8000L of water. The Aqua Dam manufacturers recommendation is that maximum water level does not exceed 75% of the total height, which totals of 45cm. This would provide us with sufficient water retention within the unit. Aqua Dam can be reused for as long as it has not suffered any structural damage to the lining. It is lightweight and can be deployed and positioned in place with 2 people. Furthermore, it will provide water containment as soon as the water starts filling it up. As the Dam is filled with water, this water can be reused for as long as it is necessary by pumping it back into the water storage containers.

Aqua Snake: Aqua Snakes will be stored in dry storage within the unit, easily accessible in case of emergency as specified within the FPP. The main use will be:
Creating temporary bunding in outside quarantine to ensure Rain water which may have come into contact with waste does not enter the environment, as well as in case any waste should require watering down due to hight temperature as specified in FPP.

- Aqua snake has a shelf life of 5 years if it has not been used. We will create a reminder on the computer calendar which is also synced with directors’ phone calendar to ensure new products are ordered a minimum of 1month prior to expiry date. Each Aqua snake measures 145cm x 25cm and weights 0.5kg. Once it has been used the bags will be disposed off with Colins Skip Hire.

- Hydro bags will be used to create temporary bunding on the back exit of the unit as well as the internal office door.  Hydro Bags have a shelf life of 5 years if they have not been used. We will create a reminder on the computer calendar which is also synced with directors’ phone calendar to ensure new products are ordered a minimum of 1 month prior to expiry date. Each Hydro bag measures 60cmx 45cm and weighs 0.5kg. Once it has been used the bags will be disposed off with Colins Skip Hire.

5.6.3 Calculating the Worst-Case Water Volume

To satisfy the regulator, you must prove your containment can handle the "worst-case scenario" (the largest possible fire).

V{total} = V{firewater} + V{rainfall}

- V{firewater}: Based on 6.6 L/min per m3 of waste.

- V{rainfall}: Based on a 1-in-100-year storm event (usually calculated as 50mm of rain over the site area).

| Component | Specification / Requirement |
| --- | --- |
| Bin Material | 4mm S235 Mild Steel (Melting Point >1,400°C) |
| Integrity | Continuous MIG weld seams (Liquid Retentive) |
| Containment | 6m separation or 120-min Fire Walls |
| Quarantine | 45 m2 clear concrete area |
| Spill Kits | Clay mats and drain bungs located within 20m of storage |
| BAY | Concrete Lego Blocks |

6. FIRE DETECTION AND SUPPRESSION

6.1 Active Monitoring

- Visual Checks: Carried out at 07:00 and 16:30 daily. During summer months, checks are more frequent between 11:00 and 16:00 to monitor building heat.

- Thermal Imaging: A 2m thermal imaging probe is used to check the core temperature of piles.

- Detection Systems: WIFI-enabled smoke and fire alarms are installed above RORO areas and 2 heat detecting CCTV pointing at wood bay

6.2 Out-of-Hours Security

- Surveillance: The site has 24/7 CCTV with night vision, linked to the owners' mobile phones for instant alerts.

- Personnel: Security personnel visit the site twice per night.

- Response Time: Owners live within 15 minutes of the site and remain on call.

7. WATER SUPPLIES

Core Fusion maintains comprehensive fire suppression capabilities with strategically located water access points and onsite equipment.

7.1 Water Supply & Fire Suppression Strategy

7.1.1 Water Supply Analysis

Core Fusion maintains a mains water supply of 18 L/min. Fire-water requirements are assessed separately for the largest indoor pile (a 30.6m³ RORO) and the largest outdoor pile (the 198m³ wood bay). The table below compares the required flow with the available mains supply and the additional flow to be provided by the hydrant.

| Waste Location | Volume (m3) | WISH Req. Flow | Mains Supply | Deficit (To be met by Hydrant) |
| --- | --- | --- | --- | --- |
| Standard Skip | 9.8m3 | 65.27 L/min | 18 L/min | 47.27 L/min |
| RORO | 30.6m3 | 203.80 L/min | 18 L/min | 185.80 L/min |
| BAY | 198m3 | 1293L/min | 18 L/min | 1,1275 L/min |

7.1.2 Suppression Strategy & Total Requirement

The design scenarios depend on waste location. The largest indoor pile is a 30.6m³ RORO, requiring approximately 203.80 L/min and 36,684 litres over three hours. The largest outdoor pile is the 198m³ wood bay, requiring 1293 L/min and 232,848 litres over three hours.

- Immediate Response (Mains): The 18 L/min supply and 2x 20m hose reels are positioned for "first-strike" capability to suppress ignitions before they escalate.

- Emergency Scale-Up (Hydrant): For the worst-case outdoor fire involving the 198m³ wood bay, the site relies on the underground hydrant located 0.2m from the boundary. The hydrant has an available flow of approximately 2,100 L/min, exceeding the required worst-case flow of 1293L/min.

7.2 Site Layout & Accessibility

The proximity of the water sources ensures that no part of the waste storage is left unprotected:

- Hydrant Proximity: Located 0.2m from the boundary.

- Internal Reach: The internal quarantine area is 52.4m from the hydrant, well within the reach of standard Fire & Rescue hose lays and onsite equipment.

- Access: Dual access via the front entrance and rear fire exit ensures that hoses can be deployed to any waste pile without obstruction.

7.3 Onsite Suppression Equipment

| Equipment Type | Specification | Quantity |
| --- | --- | --- |
| Dry Powder Extinguisher | 6kg (General use) | 6 |
| Dry Powder Extinguisher | 2kg (Vehicle-mounted) | 5 |
| CO2 Extinguisher | 2kg (Electrical/Office) | 5 |
| Fire Blanket | 1.8m x 1.8m | 2 |
| Fire Hose Reels | 20m Length | 2 |
| 1000L water tank | 8x LBC filled with water | 8 |

7.4 Water Supply Requirements

Calculations are based on WISH (Waste Industry Safety and Health) Guidance, which establishes a requirement of 6.66 L/min per 1m3 of waste (derived from a 198m3 pile requiring 1293.6 L/min).

7.4.1 Maximum Size Waste Pile

Suppression requirements are assessed separately for indoor and outdoor waste:

- Indoor scenario: 30.6m³ RORO; required flow 203.80 L/min; three-hour total 36,684 L.

- Outdoor worst-case scenario: 198m³ wood bay; required flow 1293.6 L/min.

- Outdoor three-hour total: 232,848 L. The hydrant provides approximately 2,100 L/min, exceeding the required flow by approximately 806.40 L/min.

8. Managing Fire Water Run-off

8.1 Firewater Containment & Environmental Protection

Core Fusion utilizes a multi-layered containment strategy to ensure that potentially contaminated fire water or runoff is captured onsite and disposed of safely, preventing any discharge into the local ecosystem or sewage systems.

8.1.1 Primary Containment: Front Entrance (Aqua Dam)

The main unit entrance (7m wide) will be sealed using an Aqua Dam (L: 10m x H: 60cm).

- Deployment: The dam is positioned across the entrance and filled using a dedicated onsite supply of 8,000L of clean water stored in 8x 1000L IBC tanks.

- Fill Time: Using a dedicated water pump, the dam can be deployed in approximately 9 minutes.

- Sustainability: Because the dam is filled with clean water, this water can be pumped back into the tanks for reuse once the incident is resolved.

8.1.2 Secondary Containment: Rear & External Areas

- Rear Fire Exit: Secured using Hydro Bags (L: 60cm x H: 48cm). These 0.5kg sacks are stored at the exit for rapid deployment and activate instantly upon contact with water. A minimum of two sets is maintained at this location.

- Outside Quarantine Area: To contain rainwater runoff from temporary waste storage, 18 Hydro Snakes (L: 145cm x H: 25cm) are stored at the front of the unit. These create a bunded perimeter around the skip.

  - Containment Capacity: 7m x 6m x 0.25m = 10,500L of potential runoff protection.

  - 5000L sump with designated drainage system positioned outside, serving water containment for the impermeable surface.

- Drainage Protection: 6 Neoprene drain covers are held onsite to seal internal manholes and two nearby surface water drains, preventing any ingress into the river-discharge network.

8.2 Containment Capacity Calculations (Indoor Scenario)

The containment volume is calculated based on the available "free" floor space of the unit (excluding offices, racking, and facilities) and the safe working height of the Aqua Dam (75% of its 60cm total height).

Unit Capacity Specifications

- Total Unit Area: 900m2

- Available Containment Area: 283m2 (25m x 11.32m)

- Safe Bunding Height: 45cm (75% of dam height)

- Maximum Containment Volume: 283m² × 0.45m = 127.35m³ (127,350 litres).

8.2.1 Worst-Case Scenario Analysis

For the largest indoor pile (30.6m³ RORO), the fire-suppression requirement is approximately 36,684 litres over three hours.

| Requirement | Calculation | Result |
| --- | --- | --- |
| Required Containment | Worst-case suppression flow | 36,684 L |
| Available Containment | 283m2 at 45cm depth | 127,350 L |
| Safety Margin | Available vs. Required | 347% of requirement (247% excess) |

To contain 36,684 L across 283m², the water depth would be approximately 13 cm, below the stated 45cm bunding height.

8.3 Containment Capacity Calculations (Outdoor Scenario)

The containment volume is calculated based on the available "free" floor space of the front yard (impermeable area)

Unit Capacity Specifications

- Total Yard Area: 420m2

- Available Containment Area: 420m2 (30m x 14m)

- Safe Bunding Height- Hydro Snakes: 10cm H x 45units across entrance and side would provide a total of 42,000L of water+ Gradient wood bay which provides further 25,000L of water= 107,600L of water

- Maximum Containment Volume: 12500 L (bay)+ 42,000 (yard)+ 5000 L (sump)= 59,500Litres)

8.3.1 Worst-Case Scenario Analysis

For the largest outdoor pile (198m³ wood bay), the fire-suppression requirement is approximately 1293.6 litres over three hours.

8.3.2 Outdoor Baseline Numbers

- Required 3-Hour EA Firewater: 232,848 Litres (1,293.6 L/min×180 mins)

- Outdoor Storage Capacity: 54,500 Litres (42,000L yard bund + 12,500L bay)

- Initial Fill Time (Hydrant Only): Your 54,500L outdoor capacity fills completely in 42.1 minutes (54,500÷1,293.6 L/min).

8.3.3 Hydrant Water Saved with Two Recirculation Pumps

With two 500 L/min pumps running (1,000 L/min total recirculation rate):

Total 3-Hour Suppression Demand&=232,848 LitresWater Supplied via Recirculation (180 mins @ 1,000 L/min)&=-180,000 LitresNet Fresh Hydrant Water Needed&=52,848 Litres

- Total Hydrant Input Reduction: 180,000 Litres saved (77.3% reduction).

8.4 Post-Incident Procedures & Disposal

- Water Removal: All contained fire water will be collected by an external contractor (Bio Marsh), whose vehicles are stationed adjacent to the site for rapid response.

- Tanker Access: Tankers will enter via the front yard to pump out the bunded area for legal disposal.

- Contaminated Waste: All used Hydro Bags and Hydro Snakes will be disposed of as contaminated waste ewc 19 01 11 for wood and fire debris and under hazardous for hydro snakes EWC 15 02 02.

- Recovery: Once the area is cleared of fire water, the Aqua Dam will be drained back into its storage tanks, and the neoprene covers will be cleaned and returned to storage.

9. Contingency and Recovery

- During a Fire: We will immediately stop accepting waste. Diverted loads will go to CSH Environmental and/ or Kingdom Recycling

- After a Fire: We will not restart operations until the EA and FRS have confirmed the site is safe and all fire-damaged waste has been legally disposed of.

10. Staff Training

- All staff are trained on this FPP upon induction. And toolbox talks are carried out quarterly, based on staff performance, any near miss-es and other findings during normal operating times.

- Fire drills are conducted every 3 months

- Shadowing: All new staff will be shadowing a competent member of staff for a minimum of 1 work week. This is to ensure that they are able to separate the waste correctly, recognise any non-conforming waste and to understand what is their responsibility in case of discovering a fire.

- Supervision: All staff has quarterly supervision, to ensure that they are happy in their role, to recognise and gaps in training and to offer 1-1 support due to strenuous work involving waste management. By doing so, our staff retention is great, which means that the management of waste is more efficient.

A copy of this plan is kept in the Site Office for FRS access

MAP OF YARD WITHOUT THE WOOD BAY, WASTE STORED IN CONTAINERS WITHIN THE BUILDING OR ON IMERMEABLE AREA

SITE PLAN WITH WOOD BAY, EXTENDED IMPEREAMBLE AREA AND SUMP